DeviceNetTM Conformance Composite 19 Test Results

| Test Information |
| --- |
| Test Date | 23-24 October 2007 |
| Composite Test Revision | 19 |
| ODVA File Number | 10592.01 |
| Test Type | _ Single device __ Safety Device _X_Product family* *The vendor-supplied list of product family members is attached to this report, if applicable. One instance of the remainder of this report shall be completed for each device tested. |

| Vendor Information |
| --- |
| Vendor Name | Turck, Inc. |
| Vendor Address | 5000 Fernbrook Lane, North Plymouth, MN 55446 USA |

Device Information

Device Information from Identity Object Instance 1 For multiple identity object instances, additional Device Information tables are inserted into the report. Identity Object Attribute Value 1 Vendor ID 48 2 Device Type 7 Device Profile Name General Purpose Discrete I/O 4 Product Revision 1.001 Identity Object Attribute Value for Device 1 Value for Device 2 3 Product Code(s) 1015 1016 7 Product Name(s) FDN20-32SN FDN20-16SN-16XSG

TSP 		ODVA TTC

Date		09 November 2007

Result**	Pass DeviceNet Conformance Composite 19

**All failing results are summarized and described in Table 1 at the end of the report.

10592.01 Product Family Members

The products listed in this document are regarded as the same family due to their following properties:

- Same Devicenet Firmware Version

- All DeviceNet physical layer variants submitted for test

They differ due to the following properties:

- Product Code and Product Name

- DeviceNet physical layer implementation

| Product Code | Product Name | Name of EDS File | Name of SOC File |
| --- | --- | --- | --- |
| 1015 | FDN20-32SN | FDN20-32SN_R1.eds | F1015_G.stc F1015_U.stc |
| 1016 | FDN20-16SN-16XSG | FDN20-16SN-16XSG_R1.eds | F1016_G.stc F1016_U.stc |
| 2016 | FDN20-28SN-4XSG | (not supplied) |  |
| 2017 | FDN20-20SN-12XSG | (not supplied) |  |

Conformance Test Result Details:

Device Under Test: PC =1015

Device Under Test: PC =1016

Protocol Conformance Test Revision:  A-18

| Baud Rate | SOC File *.stc | Log File *.log | Wait for explicit, ms | Wait for all, ms | Result* Pass/Fail |
| --- | --- | --- | --- | --- | --- |
| 125K | 10592_01_F1016_G1_FA_AB.stc 10592_01_F1015_U1_PA_PB_125.stc | 10592_01_F1016_G1_FA_AB.log 10592_01_F1015_U1_PA_PB_125.log | 1 | 50 | Pass |
| 250K | 10592_01_F1016_U2_PA_AB.stc 10592_01_F1015_G2_PA_PB_250.stc | 10592_01_F1016_U2_PA_AB.log 10592_01_F1015_G2_PA_PB_250.log | 1 | 50 | Pass |
| 500K | 10592_01_F1016_U5_PA_PB.stc 10592_01_F1015_G5_FA_AB_500.stc | 10592_01_F1016_U5_PA_PB.log 10592_01_F1015_G5_FA_AB_500.log | 1 | 50 | Pass |

Physical Layer Test – Revision B3

# B3-1  DeviceNet Connector

| DeviceNet Connector Criteria | Result: Pass/Fail |
| --- | --- |
| Connector matches SOC | Pass |
| Connector pins are gold colored | Pass(1) |

Note(1):  Vendor supplied ECO specifying network connectors with gold plated pins

B3-2  Bit Rates (See Physical Layer Test Revision B4, Section 5.6)

B3-3  Transmit Levels

| Transmit Level File Name | Network Voltage | Result: Pass/Fail |
| --- | --- | --- |
| Transmit level oscilloscope screens included below | 11 VDC | Pass |
| Transmit level oscilloscope screens included below | 25 VDC | Pass |

| Measured value, volts | Pass/Fail Criteria | Result: Pass/Fail |
| --- | --- | --- |
| Tests | @25V | @11V |  |  |
| Dominant level on CAN_H | Value | 4.40 | 4.46 | 3.0V<Pass<5.1V 3.0V<Warning<3.5V 4.5V<Warning<5.1V | Pass |
| Dominant level on CAN_L | Value | 2.04 | 2.12 | 0.75V<Pass<2.85V 0.75V<Warning<1.25V 2.25V<Warning<2.85V | Pass(2) |
| Recessive level on CAN_H | Value | 3.21 | 3.27 | 2.25V<Pass<3.6V 2.25V<Warning<2.7V 3.1V<Warning<3.6V | Warning(2) |
| Recessive level on CAN_L | Value | 3.21 | 3.27 | 2.25V<Pass<3.6V 2.25V<Warning<2.7V 3.1V<Warning<3.6V | Warning(2) |

| Measured value, volts | Pass/Fail Criteria | Result: Pass/Fail |
| --- | --- | --- |
| Tests | @25V | @11V |  |  |
| Dominant level Differential (CAN_H – CAN_L) | Value | 2.20 | 2.20 | 1.5V<Pass<3.0V | Pass |
| Recessive level Differential (CAN_H – CAN_L) | Value | 0.00 | 0.00 | -500mV<Pass<+50mV | Pass |

Note(2):  CAN-L dominant and CAN-H and CAN-L recessive voltages are approximately 0.4 volts greater than expected levels.  Please confirm that the miswiring diode in series with V- is a Schottky diode.

Color Key:  Yellow = CAN_H; Blue = CAN_L; Red = CAN_H – CAN_L

Color Key:  Yellow = CAN_H; Blue = CAN_L; Red = CAN_H – CAN_L

Color Key:  Yellow = CAN_H; Blue = CAN_L; Red = CAN_H – CAN_L

Note:  Yellow and Blue traces offset 1 div for viewing recessive levels

CAN-L dominant voltage from network interface card with Schottky diode (left side of oscilloscope screen above) is 0.4 volts lower than CAN-L dominant voltage from DUT (right side of screen).  The higher voltage is consistent with the use of a silicon P-N junction diode in place of a Schottky barrier diode for the reverse wiring protection diode.  DeviceNet requires a Schottky barrier diode.

B3-4  Current Drain

| Device @ Network Voltage | Average Current, A | DUT <= SOC Result: Pass/Fail |
| --- | --- | --- |
| SOC Network Current (Max) | .03 |  |
| DUT Network Current @ 25VDC | .02 | Advisory(4) |
| DUT Network Current @ 11VDC | .05 | Advisory(3,4) |

Note(3): The measured current requirement at 11 Vdc is greater than the Maximum value specified in the stc file.

Note(4):  The network power supply connections are available on I/O connector pins.  The maximum network current requirement is unknown.

B3-5  Mis-wiring (See Physical Layer Test Revision B4, Section 5.7)

B3-6  Bus Loading (No test specification)

B3-7  Network Tests (See Interoperability Test)

Physical Layer Test Revision B4

B4-5.1  Connector Style

| DeviceNet Connector Criteria | Result: Pass/Fail |
| --- | --- |
| Connector matches SOC | Pass |
| Connector pins are gold colored | Pass(1) |
| Connector type is male | Pass |

Note(1):  Vendor supplied ECO specifying network connectors with gold plated pins

B4-5.2  Indicators

| Indicator | Specified in SOC | Present in DUT | Result: Pass/Fail |
| --- | --- | --- | --- |
| Module Status LED | No | No | Pass |
| Network Status LED | No | No | Pass |
| Mod/Net LED | Yes | Yes | Pass |

B4-5.2.1  Module status LED operation (perform when MS LED is present)

| Test # | Required indicator behavior | Result: P/F |
| --- | --- | --- |
| 5.2.1 | The product contains a red/green indicator for the device status | N/A |

B4-5.2.2  Network status LED operation (perform when NS LED is present)

| Test # | Required indicator behavior | Result: Pass/Fail |
| --- | --- | --- |
| 5.2.2 | The product contains a red/green indicator for the network communication status | N/A |

B4-5.2.3  Combined Module/Network Status LED (perform if Mod/Net LED)

| Test # | Required indicator behavior | Result: Pass/Fail |
| --- | --- | --- |
| 5.2.3 | The product contains a red/green indicator for the Module/Network status | Pass |
| 5.2.3.1a | The indicator flashes green for 0.25 sec. then red for 0.25 sec during power-up self test. | Pass |
| 5.2.3.1b | The indicator is off after completion of power-up self test. | Advisory(5) |
| 5.2.3.2 | The MNS indicator flashes green after self test when DUT is a node on an occupied network and DUT MAC ID is unique. | Pass |
| 5.2.3.3 | The MNS indicator becomes solid red after a CAN_H to CAN_L short. | Pass |
| 5.2.3.3b | The DUT CAN transceiver remains recessive. | Pass |
| 5.2.3.4 | The MNS LED becomes solid red after (CAN_H, CAN_L) to (+5V, 0) | Advisory(6) |
| 5.2.3.4b | The DUT CAN transceiver remains recessive. | Advisory(6) |
|  | The NS LED becomes solid red when DUT is connected to a network where device with DUT Mac Id exists and is on-line. | Pass |

Note(5):  MNS indicator flashes amber when autobaud is enabled and baud rate is unresolved.

Note(6):  DUT stops transmitting while dominant state exists on bus but does become bus-off.  DUT resumes transmitting when dominant state is removed.

B4-5.3  Switches

| Test # | Required switch characteristics and behavior | Result: Pass/Fail |
| --- | --- | --- |
| 5.3 | Switches present on DUT match SOC | Pass |
| 5.3.1 | If MAC ID switch is rotary, thumb-wheel, or push-wheel, switch must be labeled in decimal format. | Advisory(7) |
| 5.3.2 | MSD of MAC ID switch is set to the left or top of the product. | Pass |
| 5.3.3 | Node Address Set by DIP Switch | Node Address Set by Rotary Switch | Actual MAC ID on a Network | Pass |
|  | 0 | 0 | 0 |  |
|  | 1 | 8 | 8 |  |
|  | 2 | 11 | 11 |  |
|  | 4 | 22 | 22 |  |
|  | 8 | 33 | 33 |  |
|  | 0x10 (16) | 44 | 44 |  |
|  | 0x20 (32) | 55 | 55 |  |
|  | 0x3F (63) | 63 | 63 |  |

Note(7):  MSD switch positions 8, 9 are labeled “Test”.  DeviceNet instance attribute 8 treats msd 8 as 00 and msd 9 as 01.  Switch digit 8 is not available to sw.

B4-5.4  Isolation/Impedance

Results of Vendor Supplied HIPOT Data

| Device Description | HIPOT Result +500 VDC | HIPOT Result -500 VDC |
| --- | --- | --- |
| DUT has metallic chassis not isolated from earth gnd | N/A | N/A |
| DUT has field wiring | DUT is UL and CE marked | DUT is UL and CE marked |

B4-5.4.1  Resistance and Capacitance: CAN_H to CAN_L

| Parameter | Limit | Measured | Result: Pass/Fail |
| --- | --- | --- | --- |
| CAN_H to CAN_L Resistance | 20K ohm, minimum | 38K | Pass |
| CAN_H to CAN_L Capacitance | 24 pf, maximum | 5 pF | Pass |

B4-5.5  Power

B4-5.5.1  Physical Layer Power Sense Verification

| Auxiliary Powered DUT only | Result: Pass/Fail |
| --- | --- |
| Device communicates when network power is reapplied | Pass |

B4-5.5.2  Minimum Operating Voltage

| Minimum Operating Voltage | Result |
| --- | --- |
| Device starts and operates at a network voltage of 11 VDC | Pass |

B4-5.5.3  Power Consumption (Advisory)

| Network Voltage, V | Device Voltage, V | Device network current, Amp | Device network power, W |
| --- | --- | --- | --- |
| 11 | 11 | 0.05 | Unknown(4) |
| 25 | 25 | 0.02 | Unknown(4) |

Note(4):  The network power supply connections are available on I/O connector pins.  The maximum network current requirement is unknown.

B4-5.5.4  Inrush Current (Advisory) – Duration is from peak to 37% of peak value

| Network Voltage, V | Inrush Current max, Amp | Inrush Current Duration, ms | Inrush current delay, ms |
| --- | --- | --- | --- |
| 24 | 3.6A | 0.6 | 0.5 |

Power-up / Power-down CAN Dominant

| DUT Power Event | Delay to CAN Dominant ms | CAN Dominant Duration, ms | Result: Pass/Fail |
| --- | --- | --- | --- |
| Network Power-up | None observed | N/A | Pass |
| Network Power-down | None observed | N/A | Pass |
| Aux Power-up | N/A | N/A |  |
| Aux Power-down | N/A | N/A |  |

B4-5.5.5  CAN_H and CAN_L Recessive Level Voltages

See Physical Layer Test B3, Section 3 for CAN voltage measurements.

B4-5.5.6  CAN_H and CAN_L Dominant Level Voltages

# See Physical Layer Test B3, Section 3 for CAN voltage measurements.

B4-5.5.7  CAN_H and CAN_L Differential Voltage

# See Physical Layer Test B3, Section 3 for CAN voltage measurements.

B4-5.6  CAN Timing

# B4-5.6.1  Bit Timing

| Baud Rate (Kbps) | Bit Time (us) | Result: Pass/Fail |
| --- | --- | --- |
|  | Minimum | Maximum | Measured |  |
| 125 | 7.992 | 8.008 | 8.000 | Pass |
| 250 | 3.996 | 4.004 | 4.000 | Pass |
| 500 | 1.998 | 2.002 | 2.000 | Pass |

# B4-5.6.2  Ack Delay

| Baud Rate (Kbps) | Bit Time (ns) | Result: Pass/Fail |
| --- | --- | --- |
|  | Minimum | Maximum | Measured |  |
| 500 |  | 312.5 | -10 to +90 ns | Pass |

# SOF Bit Time Jitter

| Baud Rate (Kbps) | Jitter of Dominant to Recessive Edge (p-p ns) | Result: Pass/Fail |
| --- | --- | --- |
|  | Minimum | Maximum | Measured |  |
| 500 | 0 | 4 ns | 1.6 ns | Pass |

# Bit Sample Point

| Baud Rate (Kbps) | Bit Sample Point, % Bit time | Result: Pass/Fail |
| --- | --- | --- |
|  | Transceiver delay | Minimum | Measured |  |
| 125 | 160 | 80% | 83% | Pass |
| 250 | 160 | 80% | 83% | Pass |
| 500 | 160 | 80% | 83% | Pass |

# Note(8):  Ringing noted on DUT dominant voltage levels after recessive to dominant transition.  Period is 1/520 ns = 1.92 MHz

B4-5.7  Wiring

# B4-5.7.1  Device Mis-wiring

| Step # | Verify that mis-wiring does not damage the DUT | Result: Pass/Fail |
| --- | --- | --- |
| 1 | No obvious damage during or after mis-wiring |  |
| 2 | CAN_L to CAN_H input resistance is >= 20K ohms |  |
| 3 | Device powers up and communicates on network |  |

Interoperability Conformance Test Revision C6

# Master devices used for the interoperability test

| Interoperability Master Device; P=Primary Master, A=Alternate Master |
| --- |
| Allen-Bradley 1756-DNB/A (F/W Revision 3.10) | P |
| Allen-Bradley 1747-SDN (F/W Revision 4.026) | A |
| Omron CJ1W-DRM21 (Revision 1.01) | A |

# Manager tools used for the interoperability test

| Interoperability Manager Tool; P=Primary Tool, A=Alternate Tool |
| --- |
| RSNetWorx for DeviceNet (Revision 6.00-Alpha) | P |
| CH_Studio (Revision 1.2) | A |
| Omron DeviceNet Configurator (Revision 2.21) | A |

C6-7.1  EDS File Test (Performed only if vendor supports device configuration with an EDS file.)

| No. | Test (Using Primary Manager Tool) | Result |
| --- | --- | --- |
| 1 | Install the EDS file into the Manager | Pass |
| 2 | Use the Manager to configure the DUT to use the I/O Assembly with the largest produced/consumed connection sizes referenced in the EDS file. | N/A |
| 3 | Configure the Primary Master scan list for the selected I/O configuration. | Pass |

C6-7.2  Power Cycle Test

Verify that after turning on all power supplies in each test, all of the connections are established within one (1) minute and the network returns to the “Operational” state.

C6-7.2.1  Power Supply Sequence – Slave DUT

For a DUT with a non-isolated physical layer

| Test # | Power Supply Turn ON Sequence – Primary Master – performed twice | Result: Pass/Fail |
| --- | --- | --- |
|  | 1 | 2 | 3 | 4 |  |
| 1 | Network | Master | Aux Pwd Dev | N/A | Pass |
| 2 | Network | Aux Pwd Dev | Master | N/A | Pass |
| 5 | Master | Network | Aux Pwd Dev | N/A | Pass |
| 6 | Aux Pwd Dev | Network | Master | N/A | Pass |
| 7 | Master | Aux Pwd Dev | Network | N/A | Pass |

C6-7.2.3  Power On/Off

| Test # | Power On/Off Test – Primary Master – performed 5 times | Result: Pass/Fail |
| --- | --- | --- |
| 1 | Master Power On/Off (5 times) | Pass |
| 2 | Network Power On/Off (5 times) | Pass |
| 3 | DUT Power On/Off (5 times) | N/A |

C6-7.3  Device Disconnect-Reconnect Test

| Test # | Primary Master – performed 5 times | Result: Pass/Fail |
| --- | --- | --- |
| 7.3.1 | Master Disconnect-Reconnect with time out | Pass |
| 7.3.2 | Master Disconnect-Reconnect without time out | Pass |
| 7.3.3 | DUT Disconnect-Reconnect (5 times) | Pass |

C6-7.4  Network Aerobic Test

C6-7.4.1  Master Idle/Active Test

| Step # | Primary Master – performed twice | Result: Pass/Fail |
| --- | --- | --- |
| 1 | Two successful network WHO in 5 minutes | Pass |
| 2 | Upload DUT parameters twice between WHO | Pass |
| 3 | Modify DUT parameters twice between WHO | Pass |
| 4 | Master Idle upload DUT parameters between WHO Master Idle modify DUT parameters between WHO | Pass |
| 5 | Verify network remains in “Operational State” | Pass |

| Step # | Alternate Tool – performed once | Result |
| --- | --- | --- |
| 1 | Two successful network WHO in 5 minutes | Pass |
| 2 | Upload DUT parameters twice between WHO | Pass |
| 3 | Modify DUT parameters twice between WHO | Pass |
| 4 | Master Idle upload DUT parameters between WHO Master Idle modify DUT parameters between WHO | Pass |
| 5 | Verify network remains in “Operational State” | Pass |

C6-7.4.2  Master Active Test

| Step # | Primary Master – Run time >= 1.5 hours | Result: Pass/Fail |
| --- | --- | --- |
| 1 | With Master in the Run state, network remains in the “Operational State” for 1.5 hours | Pass |

EDS File Syntax Check

| EDS File Syntax Utility WEAuth - R01.08 (Alpha) | Result: Pass/Fail |
| --- | --- |
| EDS file name | FDN20-16SN-16XSG_R1.eds FDN20-32SN_R1.eds |  |
| EDS file revision | Revision = 1.1 |  |
| Log file name | FDN20-16SN-16XSG_R1.ecf FDN20-32SN_R1.ecf | Pass |

Table 1  Conformance Failures and Advisories

| Test Item | Advisories and Failures: Observed DUT Behavior | Required Behavior & Specification Reference |
| --- | --- | --- |
| B3 – Transmit Levels | Advisory: DUT CAN-L dominant voltage level is 0.4 volts higher than expected. This behavior is consistent with the use of a silicon P-N junction diode in place of a Schottky barrier diode for the DUT reverse wiring protection diode. | Miswiring diode must be a Schottky barrier junction diode. Reference: The CIP Networks Library, Volume 3: DeviceNet Adaptation of CIP, Chapter 8: Physical Layer, Section 8-2.2 – DeviceNet Physical Layer Schematics |
| B3-4 Current Drain | Advisory: The measured current requirement at 11 Vdc is greater than the Maximum value specified in the stc file. Warning: The network power supply connections are available on I/O connector pins. Inappropriate connections to these pins may compromise the network signal integrity and network safety ground isolation. | The Max current value in the stc file should represent the maximum continuous current the DUT can draw from the network. “Important: Within a node that contains a non-isolated physical layer, … V- may connect to other external devices through … I/O connections … These external devices must be ground isolated and this requirement must be stated in the product literature of any DeviceNet product allowing this type of connection.” |
| B4-5.2.3 Combined Module/Network Status LED | Advisory: MNS indicator flashes amber when autobaud is enabled and baud rate is unresolved. | Amber and flashing amber are not DeviceNet recognized LED states. Reference: The CIP Networks Library, Volume 3: DeviceNet Adaptation of CIP, Chapter 9: Indicators and Middle Layers, Section 9-2.5 Combined Module/Network Status LED |
| B4-5.2.3 Combined Module/Network Status LED | Advisory: DUT stops transmitting while dominant state exists on bus but does become bus-off. DUT resumes transmitting when dominant state is removed. | The DUT must enter the Communication Fault state and set the Network Status LED red when a CAN Bus-Off is detected while sending Duplicate Mac Id Check Request messages. Reference: The CIP Networks Library, Volume 3: DeviceNet Adaptation of CIP, Chapter 9: Indicators and Middle Layers, Section 9-2.3: Network Status LED, Table 9-2.2 Reference: The CIP Networks Library, Volume 3: DeviceNet Adaptation of CIP, Chapter 2: DeviceNet Messaging Protocol, Section 2-3.1 State Transition Diagram & Event Matrix |
| B4-5.3 Switches | Advisory: MSD switch positions 8, 9 are labeled “Test”. Node address switch settings > 79 return values in DeviceNet instance attribute 8 in the valid mac id range of 00 to 19. |  |
| B4-5.6 CAN Timing | Advisory: Ringing noted on DUT dominant voltage levels after recessive to dominant transition. Period is 1/520 ns = 1.92 MHz | Overshoot, damping, and period may be functions of the network topology and design of other nodes. Excessive overshoot will increase the network bit error rate. |